## Cover
Calculation Revision History
Room Heating & Cooling Load Summary
Project Information
Job Title: | GPU |  |  |  |  | Rev: | P2
Job Number: | 248507 |  |  | Status: | Preliminary | Date: | 2017-06-15
General
Calculation Description |  |  |  |  | Room Heating & Cooling Load Summary
File Name |  |  |  |  | TM_Heating & Cooling.xlsx
Revision | Date | Status | Eng | Chk | Description
P1 | 2017-05-12 | Preliminary | SB | AM | Issue P1 - first iteration of detailed load calculations with building zoned to BCO guidelines
P2 | 2017-06-15 | Preliminary | SB | JQ | Issue P2 - minor updates to P1 model to ground floor only in line with architectural change - changed control setting from air temperature to dry resultant temperature
Notes

## Cooling Results
Calculation Report
Room Cooling Load Summary
Project Information
Job Title: |  | GPU | [5 empty] | Rev: | P2
Job Number: |  | 248507 |  | Status: | Preliminary |  |  | Date: | 2017-06-15
General
Description
Area / Zone / Department
IES Model File / Folder |  |  |  |  | Results File = P2 - H&C Loads.clg
Room Details |  |  |  | Design Temperature |  | IES Results |  |  |  | System Details |  |  |  | Room Outputs |  |  |  | Load Check
Level | Description |  |  |  | Area | Sensible Load | Internal Latent Gain |  | Total Load | Cooling Type | Flow Temperature | Return Temperature | System Delta T | Design margin | Required Sensible Output | Required Total Output | Flow Rate | Heat Gains | Installed Cooling | Room Group | General Notes | Lighting | Max Occupants | Equip
|  |  |  | °C | m2 | W |  |  |  |  | oC | oC | oC | % | W | W | kg/s | W/m2 | W/m2 |  |  | W/m² | m²/P | W/m²
G. | G.24 Pool Clean |  |  | 0 | 8.111 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.17 Squash Court |  |  | 0 | 65.509 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.18 Squash Court |  |  | 0 | 65.716 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Ex | Existing Changing Area |  |  | 0 | 296.65 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.15 Circulation |  |  | 0 | 33.631 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.19 Squash Court |  |  | 0 | 64.401 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.02 Circulation |  |  | 0 | 29.313 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.16 Flexible Use Area |  |  | 0 | 77.013 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.07 Dance Studio |  |  | 0 | 103.695 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Li | Lift Shaft |  |  | 0 | 6.898 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Su | Sunlight |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  | 0 | 0 | 0
Su | Sunlight |  |  | 0 | 33.337 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.01 Pool |  |  | 0 | 550.247 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.25 Pool Store |  |  | 0 | 18.262 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.23 Plant |  |  | 0 | 202.161 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.20 Gym |  |  | 0 | 342.429 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.22 Store |  |  | 0 | 21.178 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.21 Stair |  |  | 0 | 18.075 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.11 Changing Village |  |  | 0 | 265.966 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.02 Office |  |  | 0 | 15.684 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.03 Lobby |  |  | 0 | 23.535 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.29 Classroom/ Waiting Area |  |  | 0 | 45.194 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.07 WC's |  |  | 0 | 22.326 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.10 WC's |  |  | 0 | 29.596 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.08 WC's |  |  | 0 | 16.926 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.09 WC's |  |  | 0 | 54.031 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Vo | Void |  |  | 0 | 1.383 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Li | Lift Shaft |  |  | 0 | 5.264 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.21 Stair |  |  | 0 | 18.075 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.10 Classroom |  |  | 0 | 67.598 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.05 Store |  |  | 0 | 11.911 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.06 Store |  |  | 0 | 7.249 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.13 Accessible W.C. |  |  | 0 | 4.532 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.12 Accessible Changing Room |  |  | 0 | 7.784 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.11 Store |  |  | 0 | 6.826 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.16 Female WC's |  |  | 0 | 20.708 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.15 Male WC's |  |  | 0 | 20.742 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.03 Fitness Centre |  |  | 0 | 313.315 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.01 Circulation |  |  | 0 | 201.314 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.08 Health Related Fitness |  |  | 0 | 105.542 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.09 HRE office |  |  | 0 | 10.206 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Su | Sunlight |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  | 0 | 0 | 0
Su | Sunlight |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  | 0 | 0 | 0
Su | Sunlight |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 16 | 22 | 6 | 15% | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  | 0 | 0 | 0
G. | G.05 Reception Desk |  |  | 0 | 12.85 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.26 Circulation |  |  | 0 | 273.225 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.14a Showers |  |  | 0 | 21.354 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.14 Male Changing |  |  | 0 | 37.432 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.17 Female Changing |  |  | 0 | 37.658 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.17a Showers |  |  | 0 | 21.483 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
G. | G.06 Waiting Area |  |  | 0 | 116.142 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
F. | F.19 Refuge |  |  | 0 | 17.117 | 0 | 0 |  | 0 |  | 6 | 12 | 6 | 15% | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  | Total Load (kW) |  |  | 0 | 0 |  | 0 |  |  | Total Load (kW) |  |  |  | 0
|  |  | Total Load (W/m2) |  |  | 0 |  |  | 0 |  |  | Total Load (W/m2) |  |  |  | 0
[5 empty] | Diversified Sensible Load (kW) | [5 empty] | Diversified Sensible Load & Margin (kW) |  |  |  |  | 0
Diversified Latent Gain (kW)
[5 empty] | Diversified Total Load (kW) |  |  | 0 |  |  | Diversified Sensible Load & Margin (kW) |  |  |  |  | 0
Edit as appropriate to summarise:
External design temp based upon 30 deg C db, 20 wb
Infiltration based on 0.25ACH
No mechanical ventilation load included (assumed dealt with at AHU)
Occupant gains are 75W/P sensible, 55W/P latent. Latent load taken by AHU.
Ocupant and Equipment Changes have been made at room level (not template)
10W/m2 lighting
25W/m2 equipment
Occupancy times = 9am-6pm (constant, no diversity)
Surrounding rooms have run as programmed (i.e. no upper limit has been artificially been imposed)
Usage Instructions
Please paste data into "Full IES Export Tab" as indicated within the tab - both cooling loads and room areas are required (this can be obtained from tabular room data within ModelIT). It would be wise to restrict this selection just to the rooms requiring cooling.
Lighting, occupancy and equipment (columns AJ, AK, AL) must be input manually - tabular room data can assist with this.
Rooms with a decimal cooling setupoint are actually uncooled spaces - and hence highlighted in blue in the Room Outputs section.
Conditional formatting is not setup on this sheet as each space should be carefully examined, however anything greater than 120W/m2 should be checked for accuracy.
Steve B - 1/07/2014
Diversified load accounts for the solar gains around the building (i.e. only one "half" will be heated simultaneously) - and therefore the peak recorded load for the building is expressed here.
This may help in sizing the primary circuit/selecting the chillers
Latent gain has been added to the sensible cooling load to estimate the total cooling load (this presents the worst case analysis at the moment)
Note on Z64: Paul Newnham: m3/s (post room is cooled via air not water.

## Heating Results
Calculation Report
Room Heat Loss Summary
Project Information
Job Title: |  | GPU |  |  |  |  | Rev: | P2
Job Number: |  | 248507 | Status: | Preliminary |  |  | Date: | 2017-06-15
General
Description
Area / Zone / Department
IES Model File / Folder |  |  |  | Results File = P2 - H&C Loads.htg
Room Details |  |  |  |  | IES Results |  |  |  | System Details |  |  |  | Room Outputs |  |  | Load Check
Level | Description |  | Setpoint | Area | Fabric Loss | Infiltration Loss | Auxiliary Ventilation | Total Loss | Heating Type | Flow Temperature | Return Temperature | System Delta T | Design margin | Required Output | Flow Rate | Heat Loss | Installed Heating | Room Group | General Notes
|  |  | °C | m2 | W | W | W | W |  | oC | oC | oC | % | W | kg/s | W/m2 | W/m2
G. | G.24 Pool Clean |  | 17.34 | 8.111 | 392.9 | 66.1 | 0 | 459 |  | 80 | 60 | 20 | 15% | 527.85 | 0.007 | 56.5898 | 65.0783 | 0
G. | G.17 Squash Court |  | 14.89 | 65.509 | 517.1 | 1101.5 | 0 | 1618.6 |  | 80 | 60 | 20 | 15% | 1861.39 | 0.023 | 24.7081 | 28.4143 | 0
G. | G.18 Squash Court |  | 14.91 | 65.716 | 461.5 | 1105 | -881.2 | 685.3 |  | 80 | 60 | 20 | 15% | 788.095 | 0.01 | 10.4282 | 11.9924 | 0
Ex | Existing Changing Area |  | 18.79 | 296.65 | 2860.2 | 2524.1 | -884 | 4500.3 |  | 80 | 60 | 20 | 15% | 5175.345 | 0.062 | 15.1704 | 17.446 | 0
G. | G.15 Circulation |  | 17.77 | 33.631 | 525.8 | 274.2 | 0 | 800 |  | 80 | 60 | 20 | 15% | 920 | 0.011 | 23.7876 | 27.3557 | 0
G. | G.19 Squash Court |  | 14.81 | 64.401 | 848.2 | 1082.9 | 0 | 1931.1 |  | 80 | 60 | 20 | 15% | 2220.765 | 0.027 | 29.9856 | 34.4834 | 0
F. | F.02 Circulation |  | 17.9 | 29.313 | 239.3 | 214.4 | -866.3 | -412.6 |  | 80 | 60 | 20 | 15% | -474.49 | -0.006 | -14.0757 | -16.187 | 0
G. | G.16 Flexible Use Area |  | 15.83 | 77.013 | 1401.5 | 1247 | 0 | 2648.5 |  | 80 | 60 | 20 | 15% | 3045.775 | 0.037 | 34.3903 | 39.5488 | 0
F. | F.07 Dance Studio |  | 23.8 | 103.695 | 3087.4 | 956.3 | 0 | 4043.7 |  | 80 | 60 | 20 | 15% | 4650.255 | 0.056 | 38.9961 | 44.8455 | 0
Li | Lift Shaft |  | 16.99 | 6.898 | -47.7 | 47.9 | 4891.2 | 4891.4 |  | 80 | 60 | 20 | 15% | 5625.11 | 0.068 | 709.1041 | 815.4697 | 0
Su | Sunlight |  | 13.48 | 0 | -19 | 19 | 0 | -1.7764e-14 |  | 80 | 60 | 20 | 15% | -2.0428e-14 | -0.001 | #DIV/0! | #DIV/0! | 0
Su | Sunlight |  | 3.74 | 33.337 | -21.4 | 21.4 | 0 | -3.1974e-14 |  | 80 | 60 | 20 | 15% | -3.6771e-14 | -0.001 | -9.5913e-16 | -1.103e-15 | 0
G. | G.01 Pool |  | 28.7 | 550.247 | 21198.4 | 16290.9 | 0 | 37489.3 |  | 80 | 60 | 20 | 15% | 43112.695 | 0.515 | 68.1318 | 78.3515 | 0
G. | G.25 Pool Store |  | 17.47 | 18.262 | 565.8 | 148.9 | 0 | 714.7 |  | 80 | 60 | 20 | 15% | 821.905 | 0.01 | 39.1359 | 45.0063 | 0
G. | G.23 Plant |  | 9.78 | 202.161 | 1799.1 | 1075.1 | 0 | 2874.2 |  | 80 | 60 | 20 | 15% | 3305.33 | 0.04 | 14.2174 | 16.35 | 0
G. | G.20 Gym |  | 15.69 | 342.429 | 6690.2 | 6445.9 | 0 | 13136.1 |  | 80 | 60 | 20 | 15% | 15106.515 | 0.181 | 38.3615 | 44.1158 | 0
G. | G.22 Store |  | 17.47 | 21.178 | 652.5 | 172.7 | 0 | 825.2 |  | 80 | 60 | 20 | 15% | 948.98 | 0.012 | 38.965 | 44.8097 | 0
G. | G.21 Stair |  | 17.46 | 18.075 | 588.1 | 147.4 | 0 | 735.5 |  | 80 | 60 | 20 | 15% | 845.825 | 0.011 | 40.6916 | 46.7953 | 0
G. | G.11 Changing Village |  | 24.25 | 265.966 | 6266.2 | 2828.8 | 0 | 9095 |  | 80 | 60 | 20 | 15% | 10459.25 | 0.125 | 34.1961 | 39.3255 | 0
G. | G.02 Office |  | 20.24 | 15.684 | 814.2 | 144.6 | 0 | 958.8 |  | 80 | 60 | 20 | 15% | 1102.62 | 0.014 | 61.1324 | 70.3022 | 0
G. | G.03 Lobby |  | 17.16 | 23.535 | 1066.9 | 191.9 | 244.6 | 1503.4 |  | 80 | 60 | 20 | 15% | 1728.91 | 0.021 | 63.8793 | 73.4612 | 0
G. | G.29 Classroom/ Waiting Area |  | 19.11 | 45.194 | 356.9 | 384.5 | 0 | 741.4 |  | 80 | 60 | 20 | 15% | 852.61 | 0.011 | 16.4048 | 18.8656 | 0
G. | G.07 WC's |  | 18.98 | 22.326 | 102.6 | 190 | 917.1 | 1209.7 |  | 80 | 60 | 20 | 15% | 1391.155 | 0.017 | 54.1835 | 62.311 | 0
G. | G.10 WC's |  | 18.93 | 29.596 | 194.9 | 251.8 | 0 | 446.7 |  | 80 | 60 | 20 | 15% | 513.705 | 0.007 | 15.0933 | 17.3572 | 0
G. | G.08 WC's |  | 18.98 | 16.926 | 78.8 | 144 | 0 | 222.8 |  | 80 | 60 | 20 | 15% | 256.22 | 0.004 | 13.1632 | 15.1377 | 0
G. | G.09 WC's |  | 18.91 | 54.031 | 399.3 | 459.7 | 0 | 859 |  | 80 | 60 | 20 | 15% | 987.85 | 0.012 | 15.8983 | 18.283 | 0
Vo | Void |  | 17.84 | 1.383 | -10.9 | 11.2 | 0 | 0.3 |  | 80 | 60 | 20 | 15% | 0.345 | 0.001 | 0.21692 | 0.24946 | 0
Li | Lift Shaft |  | 17.31 | 5.264 | -41 | 41.4 | 0 | 0.4 |  | 80 | 60 | 20 | 15% | 0.46 | 0.001 | 0.075988 | 0.087386 | 0
F. | F.21 Stair |  | 17.57 | 18.075 | 482.1 | 147.4 | 0 | 629.5 |  | 80 | 60 | 20 | 15% | 723.925 | 0.009 | 34.8271 | 40.0512 | 0
F. | F.10 Classroom |  | 18.86 | 67.598 | 1085.8 | 515.9 | 0 | 1601.7 |  | 80 | 60 | 20 | 15% | 1841.955 | 0.022 | 23.6945 | 27.2487 | 0
F. | F.05 Store |  | 17.87 | 11.911 | 127.9 | 87.1 | 1283.9 | 1498.9 |  | 80 | 60 | 20 | 15% | 1723.735 | 0.021 | 125.8417 | 144.7179 | 0
F. | F.06 Store |  | 17.89 | 7.249 | 78.5 | 53 | 0 | 131.5 |  | 80 | 60 | 20 | 15% | 151.225 | 0.002 | 18.1404 | 20.8615 | 0
F. | F.13 Accessible W.C. |  | 18.83 | 4.532 | 77.3 | 34.6 | 0 | 111.9 |  | 80 | 60 | 20 | 15% | 128.685 | 0.002 | 24.6911 | 28.3947 | 0
F. | F.12 Accessible Changing Room |  | 18.81 | 7.784 | 121 | 59.4 | 0 | 180.4 |  | 80 | 60 | 20 | 15% | 207.46 | 0.003 | 23.1757 | 26.6521 | 0
F. | F.11 Store |  | 17.92 | 6.826 | 59.2 | 49.9 | 0 | 109.1 |  | 80 | 60 | 20 | 15% | 125.465 | 0.002 | 15.983 | 18.3805 | 0
F. | F.16 Female WC's |  | 18.92 | 20.708 | 141.6 | 158.1 | 0 | 299.7 |  | 80 | 60 | 20 | 15% | 344.655 | 0.005 | 14.4727 | 16.6436 | 0
F. | F.15 Male WC's |  | 18.92 | 20.742 | 142.1 | 158.3 | 0 | 300.4 |  | 80 | 60 | 20 | 15% | 345.46 | 0.005 | 14.4827 | 16.6551 | 0
F. | F.03 Fitness Centre |  | 15.81 | 313.315 | 2384 | 2092.4 | 0 | 4476.4 |  | 80 | 60 | 20 | 15% | 5147.86 | 0.062 | 14.2872 | 16.4303 | 0
F. | F.01 Circulation |  | 17.96 | 201.314 | 1773.9 | 1564.7 | 0 | 3338.6 |  | 80 | 60 | 20 | 15% | 3839.39 | 0.046 | 16.584 | 19.0716 | 0
F. | F.08 Health Related Fitness |  | 15.85 | 105.542 | 759.4 | 704.8 | 1956.5 | 3420.7 |  | 80 | 60 | 20 | 15% | 3933.805 | 0.047 | 32.4108 | 37.2724 | 0
F. | F.09 HRE office |  | 20.42 | 10.206 | 381.5 | 84.4 | 0 | 465.9 |  | 80 | 60 | 20 | 15% | 535.785 | 0.007 | 45.6496 | 52.4971 | 0
Su | Sunlight |  | 13.48 | 0 | -19 | 19 | 0 | -1.7764e-14 |  | 80 | 60 | 20 | 15% | -2.0428e-14 | -0.001 | #DIV/0! | #DIV/0! | 0
Su | Sunlight |  | 8.11 | 0 | -9.8 | 9.8 | 0 | -3.5527e-15 |  | 80 | 60 | 20 | 15% | -4.0856e-15 | -0.001 | #DIV/0! | #DIV/0! | 0
Su | Sunlight |  | 8.11 | 0 | -9.8 | 9.8 | 0 | -3.5527e-15 |  | 80 | 60 | 20 | 15% | -4.0856e-15 | -0.001 | #DIV/0! | #DIV/0! | 0
G. | G.05 Reception Desk |  | 20.55 | 12.85 | 396 | 118.4 | 0 | 514.4 |  | 80 | 60 | 20 | 15% | 591.56 | 0.008 | 40.0311 | 46.0358 | 0
G. | G.26 Circulation |  | 17.95 | 273.225 | 1439.6 | 2227.9 | 0 | 3667.5 |  | 80 | 60 | 20 | 15% | 4217.625 | 0.051 | 13.423 | 15.4365 | 0
F. | F.14a Showers |  | 18.78 | 21.354 | 274 | 163 | 0 | 437 |  | 80 | 60 | 20 | 15% | 502.55 | 0.007 | 20.4645 | 23.5342 | 0
F. | F.14 Male Changing |  | 18.87 | 37.432 | 297.8 | 285.7 | 0 | 583.5 |  | 80 | 60 | 20 | 15% | 671.025 | 0.009 | 15.5883 | 17.9265 | 0
F. | F.17 Female Changing |  | 18.88 | 37.658 | 288.9 | 287.4 | 0 | 576.3 |  | 80 | 60 | 20 | 15% | 662.745 | 0.008 | 15.3035 | 17.599 | 0
F. | F.17a Showers |  | 18.78 | 21.483 | 272.1 | 164 | 0 | 436.1 |  | 80 | 60 | 20 | 15% | 501.515 | 0.006 | 20.2998 | 23.3447 | 0
G. | G.06 Waiting Area |  | 17.89 | 116.142 | 1044.8 | 947 | 0 | 1991.8 |  | 80 | 60 | 20 | 15% | 2290.57 | 0.028 | 17.1497 | 19.7222 | 0
F. | F.19 Refuge |  | 17.8 | 17.117 | 219.6 | 125.2 | 489.1 | 833.9 |  | 80 | 60 | 20 | 15% | 958.985 | 0.012 | 48.7176 | 56.0253 | 0
47655.8
[5 empty] | Total Load (kW) |  |  | 117.583 |  | Total Load & Margin (kW) |  |  |  | 135.2204
[5 empty] | Total Load (W/m2) |  |  | 31.3589 |  | Total Load & Margin (W/m2) |  |  |  | 36.0627
Edit as appropriate to summarise:
External design temp based upon -4 deg C
Infiltration based on 0.25ACH
Usage Instructions
Please paste data into "Full IES Export Tab" as indicated within the tab - both heating loads and room areas are required (this can be obtained from tabular room data within ModelIT)
Rooms with a decimal heating setupoint are actually unheated spaces - and hence highlighted in blue in the Room Outputs section.
Conditional formatting is setup on the "Installed heating" to check for loads greater than 70W/m2 - we should be cautious if values are significantly higher than this.
Steve B - 1/07/2014

## RAW IES Results
Paste Room Schedule Here (Cell A2): | [12 empty] | Paste Space Groups Here (Cell O2): |  |  |  |  | Paste Cooling Schedule From VistaPro Here (Cell U2): | [8 empty] | Paste Internal Latent Peak Schedule From VistaPro Here (Cell AE2): |  |  |  |  | Paste Reference Internal Gains Schedule From Tabular Room Data Here (Cell AK2): | [8 empty] | Paste Heating Schedule From VistaPro Here (Cell AU2): | [11 empty] | For GPU - Control via dry resultant
Space ID | Space # (Real) | Space Name (Real) | Min. Height (m) (Real) | Max. Height (m) (Real) | Volume (m³) (Real) | Floor Area (m²) (Real) | Floor Perimeter (m) (Real) | Floor Lettable Area (%) (Real) | Floor Circulation Area (%) (Real) | Ext. Wall Area (m²) (Real) | Ext. Opening Area (m²) (Real) | Include in building floor area? (Real) | Space ID | Space # (Real) | Space Name (Real) | Floors (Grouping Scheme) (Real) | Activities (Grouping Scheme) (Real) |  | Peak Date | Peak Time | Air temperature (°C) | Cooling plant sensible load (kW) | Dehumidification plant load (kW) | Cooling + dehum plant load (kW) | Space conditioning latent (kW) | Space conditioning sensible (kW) |  | Peak Date | Peak Time | Cooling plant sensible load (kW) | Internal latent gain (kW) | Space ID | Space # (Real) | Space Name (Real) | Gain 1 Reference (Real) | Gain 1 Max. Sensible Gain (W/m²) (Real) | Gain 2 Reference (Real) | Gain 2 Occupancy (m²/person) (Real) | Gain 3 Reference (Real) | Gain 3 Max. Sensible Gain (W/m²) (Real) |  | Air temperature (°C) | Dry resultant temperature (°C) | External conduction gain (kW) | Internal conduction gain (kW) | Air system input sensible (kW) | Aux vent gain (kW) | Infiltration gain (kW) | Natural vent gain (kW) | Space conditioning sensible (kW) | Steady state heating plant load (kW) | DHW heating demand (kW) |  | Peak Date | Peak Time | Dry resultant temperature (°C) | Cooling plant sensible load (kW)
PL000000 | 0 | G.24 Pool Clean | 0 | 4.175 | 33.863 | 8.111 | 11.5 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [29 empty] | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg | Stage 4 Heating Load Calc - AR.htg
SQ000000 | 1 | G.17 Squash Court | 0 | 10.166 | 648.601 | 65.509 | 33.06 | 100 <from template> | 0 <from template> | 19.685 | 0 | Yes <from template> | [28 empty] | G.24 Pool Clean | 18 | 17.34 | -0.0594 | -0.3335 | 0 | 0 | -0.0661 | 0 | 0.459 | 0.459 | 0
SQ000001 | 2 | G.18 Squash Court | 0 | 10.166 | 650.659 | 65.716 | 33.1 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.17 Squash Court | 15 | 14.89 | -0.5171 | 0 | 0 | 0.8812 | -1.1015 | 0 | 0.7375 | 0.737 | 0
XS000000 | 3 | Existing Changing Area | 0 | 4.175 | 1238.516 | 296.65 | 89.58 | 100 <from template> | 0 <from template> | 66.738 | 0 | Yes <from template> | [28 empty] | G.18 Squash Court | 15 | 14.91 | -0.4331 | -0.0284 | 0 | 0.884 | -1.105 | 0 | 0.6825 | 0.682 | 0
CR000001 | 4 | G.15 Circulation | 0 | 4.175 | 140.411 | 33.631 | 32.55 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | Existing Changing Area | 19 | 18.79 | -1.9092 | -0.951 | 0 | 0 | -2.5241 | 0 | 5.3843 | 5.384 | 0
SQ000002 | 5 | G.19 Squash Court | 0 | 10.166 | 637.638 | 64.401 | 32.84 | 100 <from template> | 0 <from template> | 98.387 | 0 | Yes <from template> | [28 empty] | G.15 Circulation | 18 | 17.77 | -0.1387 | -0.3871 | 0 | 0 | -0.2742 | 0 | 0.8 | 0.8 | 0
CR000003 | 6 | F.02 Circulation | 4.175 | 7.92 | 109.776 | 29.313 | 30.22 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.19 Squash Court | 15 | 14.81 | -0.8482 | 0 | 0 | 0.8663 | -1.0829 | 0 | 1.0648 | 1.065 | 0
FL000002 | 7 | G.16 Flexible Use Area | 0 | 9.636 | 699.283 | 77.013 | 47.2 | 100 <from template> | 0 <from template> | 86.412 | 3.819 | Yes <from template> | [28 empty] | F.02 Circulation | 18 | 17.9 | -0.1003 | -0.139 | 0 | 0 | -0.2144 | 0 | 0.4537 | 0.454 | 0
DN000002 | 8 | F.07 Dance Studio | 4.175 | 7.92 | 388.338 | 103.695 | 40.81 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.16 Flexible Use Area | 16 | 15.83 | -1.0626 | -0.3389 | 0 | 0 | -1.247 | 0 | 2.6485 | 2.649 | 0
HL000000 | 9 | Lift Shaft | 4.175 | 7.92 | 25.832 | 6.898 | 10.51 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.07 Dance Studio | 24 | 23.8 | -0.3224 | -2.765 | 0 | -4.8912 | -0.9563 | 0 | 8.9348 | 8.935 | 0
BL000000 | 10 | Sunlight | 7.92 | 8.82 | 12.195 | 0 | 18.5 | 100 <from template> | 0 <from template> | 15.729 | 12.25 | Yes <from template> | [28 empty] | Lift Shaft | 16.84 | 16.99 | -0.0228 | 0.0705 | 0 | 0 | -0.0479 | 0 | 0 | 0 | 0
BL000002 | 11 | Sunlight | 7.92 | 8.89 | 29.003 | 33.337 | 35.92 | 100 <from template> | 0 <from template> | 31.253 | 29.26 | Yes <from template> | [28 empty] | Sunlight | 13.38 | 13.48 | -0.432 | 0.451 | 0 | 0 | -0.019 | 0 | 0 | 0 | 0
PL000003 | 12 | G.01 Pool | 0 | 11.226 | 5560.728 | 550.247 | 98.72 | 100 <from template> | 0 <from template> | 654.665 | 86.36 | Yes <from template> | [28 empty] | Sunlight | 3.7 | 3.74 | -0.4745 | 0.4959 | 0 | 0 | -0.0214 | 0 | 0 | 0 | 0
PL000001 | 13 | G.25 Pool Store | 0 | 4.175 | 76.246 | 18.262 | 17.71 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.01 Pool | 29.5 | 28.7 | -14.7969 | -6.4015 | 0 | 0 | -16.2909 | 0 | 37.4893 | 37.489 | 0
PL000004 | 14 | G.23 Plant | 0 | 4.175 | 844.023 | 202.161 | 75.42 | 100 <from template> | 0 <from template> | 150.809 | 16.556 | Yes <from template> | [28 empty] | G.25 Pool Store | 18 | 17.47 | -0.1349 | -0.4309 | 0 | 0 | -0.1489 | 0 | 0.7147 | 0.715 | 0
GY000000 | 15 | G.20 Gym | 0 | 10.946 | 3614.686 | 342.429 | 76.76 | 100 <from template> | 0 <from template> | 463.787 | 67.669 | Yes <from template> | [28 empty] | G.23 Plant | 10 | 9.78 | -1.7991 | 0 | 0 | 0 | -1.0751 | 0 | 2.8741 | 2.874 | 0
ZZ000000 | 16 | G.22 Store | 0 | 4.175 | 88.418 | 21.178 | 20.42 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.20 Gym | 16 | 15.69 | -6.4025 | -0.2877 | 0 | 0 | -6.4459 | 0 | 13.136 | 13.136 | 0
ZZ000001 | 17 | G.21 Stair | 0 | 4.175 | 75.463 | 18.075 | 18.28 | 100 <from template> | 0 <from template> | 38.15 | 5.651 | Yes <from template> | [28 empty] | G.22 Store | 18 | 17.47 | -0.0858 | -0.5667 | 0 | 0 | -0.1727 | 0 | 0.8252 | 0.825 | 0
WT000001 | 18 | G.11 Changing Village | 0 | 4.175 | 1110.406 | 265.966 | 65.84 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.21 Stair | 18 | 17.46 | -0.5048 | -0.0833 | 0 | 0 | -0.1474 | 0 | 0.7355 | 0.735 | 0
LB000000 | 19 | G.02 Office | 0 | 4.175 | 65.482 | 15.684 | 16.26 | 100 <from template> | 0 <from template> | 36.976 | 9.715 | Yes <from template> | [28 empty] | G.11 Changing Village | 25 | 24.25 | -1.4018 | -4.8644 | 0 | 0 | -2.8288 | 0 | 9.095 | 9.095 | 0
LB000003 | 20 | G.03 Lobby | 0 | 4.175 | 98.259 | 23.535 | 21.34 | 100 <from template> | 0 <from template> | 31.535 | 25.303 | Yes <from template> | [28 empty] | G.02 Office | 21 | 20.24 | -0.7073 | -0.1069 | 0 | -0.2446 | -0.1446 | 0 | 1.2033 | 1.203 | 0
LB000004 | 21 | G.29 Classroom/ Waiting Area | 0 | 4.175 | 188.686 | 45.194 | 27.36 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.03 Lobby | 18 | 17.16 | -1.0669 | 0 | 0 | 0 | -0.1919 | 0 | 1.2588 | 1.259 | 0
LB000007 | 22 | G.07 WC's | 0 | 4.175 | 93.21 | 22.326 | 19 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.29 Classroom/ Waiting Area | 19 | 19.11 | -0.1984 | -0.1585 | 0 | -0.9171 | -0.3845 | 0 | 1.6585 | 1.659 | 0
LB000005 | 23 | G.10 WC's | 0 | 4.175 | 123.562 | 29.596 | 22.41 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.07 WC's | 19 | 18.98 | -0.0973 | -0.0053 | 0 | 0 | -0.19 | 0 | 0.2925 | 0.292 | 0
LB000008 | 24 | G.08 WC's | 0 | 4.175 | 70.667 | 16.926 | 16.47 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.10 WC's | 19 | 18.93 | -0.1286 | -0.0663 | 0 | 0 | -0.2518 | 0 | 0.4467 | 0.447 | 0
LB000009 | 25 | G.09 WC's | 0 | 4.175 | 225.58 | 54.031 | 36.27 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.08 WC's | 19 | 18.98 | -0.0737 | -0.0051 | 0 | 0 | -0.144 | 0 | 0.2228 | 0.223 | 0
LB000006 | 26 | Void | 0 | 4.175 | 5.773 | 1.383 | 5.1 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.09 WC's | 19 | 18.91 | -0.2345 | -0.1648 | 0 | 0 | -0.4597 | 0 | 0.859 | 0.859 | 0
LB00000A | 27 | Lift Shaft | 0 | 4.175 | 21.976 | 5.264 | 9.49 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | Void | 17.76 | 17.84 | -0.0057 | 0.0166 | 0 | 0 | -0.0112 | 0 | 0 | 0 | 0
ZZ000002 | 28 | F.21 Stair | 4.175 | 8.35 | 75.463 | 18.075 | 18.28 | 100 <from template> | 0 <from template> | 39.395 | 2.321 | Yes <from template> | [28 empty] | Lift Shaft | 17.18 | 17.31 | -0.0214 | 0.0624 | 0 | 0 | -0.0414 | 0 | 0 | 0 | 0
CL000000 | 29 | F.10 Classroom | 4.175 | 7.92 | 253.154 | 67.598 | 32.97 | 100 <from template> | 0 <from template> | 28.626 | 19.788 | Yes <from template> | [28 empty] | F.21 Stair | 18 | 17.57 | -0.3559 | -0.1262 | 0 | 0 | -0.1474 | 0 | 0.6295 | 0.63 | 0
23000000 | 30 | F.05 Store | 4.175 | 7.92 | 44.605 | 11.911 | 15.91 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.10 Classroom | 19 | 18.86 | -1.0245 | -0.0613 | 0 | -1.2839 | -0.5159 | 0 | 2.8857 | 2.886 | 0
ST000000 | 31 | F.06 Store | 4.175 | 7.92 | 27.148 | 7.249 | 11.25 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.05 Store | 18 | 17.87 | -0.0407 | -0.0872 | 0 | 0 | -0.0871 | 0 | 0.2151 | 0.215 | 0
HL000006 | 32 | F.13 Accessible W.C. | 4.175 | 7.92 | 16.971 | 4.532 | 8.83 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.06 Store | 18 | 17.89 | -0.0248 | -0.0537 | 0 | 0 | -0.053 | 0 | 0.1315 | 0.132 | 0
HL000007 | 33 | F.12 Accessible Changing Room | 4.175 | 7.92 | 29.151 | 7.784 | 11.16 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.13 Accessible W.C. | 19 | 18.83 | -0.0161 | -0.0612 | 0 | 0 | -0.0346 | 0 | 0.1119 | 0.112 | 0
HL000008 | 34 | F.11 Store | 4.175 | 7.92 | 25.562 | 6.826 | 10.47 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.12 Accessible Changing Room | 19 | 18.81 | -0.0276 | -0.0934 | 0 | 0 | -0.0594 | 0 | 0.1804 | 0.18 | 0
HL00000D | 35 | F.16 Female WC's | 4.175 | 7.92 | 77.553 | 20.708 | 18.43 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.11 Store | 18 | 17.92 | -0.0234 | -0.0358 | 0 | 0 | -0.0499 | 0 | 0.1091 | 0.109 | 0
HL00000B | 36 | F.15 Male WC's | 4.175 | 7.92 | 77.677 | 20.742 | 18.44 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.16 Female WC's | 19 | 18.92 | -0.074 | -0.0676 | 0 | 0 | -0.1581 | 0 | 0.2997 | 0.3 | 0
ST000001 | 37 | F.03 Fitness Centre | 4.175 | 7.92 | 1173.365 | 313.315 | 74.96 | 100 <from template> | 0 <from template> | 68.012 | 21.588 | Yes <from template> | [28 empty] | F.15 Male WC's | 19 | 18.92 | -0.0742 | -0.0679 | 0 | 0 | -0.1583 | 0 | 0.3004 | 0.3 | 0
HL000009 | 38 | F.01 Circulation | 4.175 | 7.92 | 801.165 | 201.314 | 115.98 | 100 <from template> | 0 <from template> | 41.746 | 11.903 | Yes <from template> | [28 empty] | F.03 Fitness Centre | 16 | 15.81 | -1.885 | -0.499 | 0 | 0 | -2.0924 | 0 | 4.4764 | 4.476 | 0
HL000002 | 39 | F.08 Health Related Fitness | 4.175 | 7.92 | 395.256 | 105.542 | 45.07 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.01 Circulation | 18 | 17.96 | -1.2058 | -0.5681 | 0 | -1.9565 | -1.5647 | 0 | 5.2951 | 5.295 | 0
F0000000 | 40 | F.09 HRE office | 4.175 | 7.92 | 38.22 | 10.206 | 13.1 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.08 Health Related Fitness | 16 | 15.85 | -0.2635 | -0.4959 | 0 | 0 | -0.7048 | 0 | 1.4642 | 1.464 | 0
SN000000 | 41 | Sunlight | 7.92 | 8.82 | 12.195 | 0 | 18.5 | 100 <from template> | 0 <from template> | 15.729 | 12.25 | Yes <from template> | [28 empty] | F.09 HRE office | 21 | 20.42 | -0.0385 | -0.343 | 0 | 0 | -0.0844 | 0 | 0.4659 | 0.466 | 0
SN000002 | 42 | Sunlight | 7.92 | 8.82 | 8.875 | 0 | 14.54 | 100 <from template> | 0 <from template> | 12.359 | 9.5 | Yes <from template> | [28 empty] | Sunlight | 13.38 | 13.48 | -0.432 | 0.451 | 0 | 0 | -0.019 | 0 | 0 | 0 | 0
SN000001 | 43 | Sunlight | 7.92 | 8.82 | 8.875 | 0 | 14.54 | 100 <from template> | 0 <from template> | 12.359 | 9.5 | Yes <from template> | [28 empty] | Sunlight | 8.04 | 8.11 | -0.2367 | 0.2465 | 0 | 0 | -0.0098 | 0 | 0 | 0 | 0
LB000002 | 44 | G.05 Reception Desk | 0 | 4.175 | 53.649 | 12.85 | 15.5 | 100 <from template> | 0 <from template> | 23.587 | 0 | Yes <from template> | [28 empty] | Sunlight | 8.04 | 8.11 | -0.2367 | 0.2465 | 0 | 0 | -0.0098 | 0 | 0 | 0 | 0
G2000002 | 45 | G.26 Circulation | 0 | 4.175 | 1140.714 | 273.225 | 148.27 | 100 <from template> | 0 <from template> | 33.4 | 0 | Yes <from template> | [28 empty] | G.05 Reception Desk | 21 | 20.55 | -0.2398 | -0.1562 | 0 | 0 | -0.1184 | 0 | 0.5145 | 0.514 | 0
HL00000A | 46 | F.14a Showers | 4.175 | 7.92 | 79.97 | 21.354 | 18.79 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | G.26 Circulation | 18 | 17.95 | -1.3279 | -0.1117 | 0 | 0 | -2.2279 | 0 | 3.6675 | 3.667 | 0
F1000000 | 47 | F.14 Male Changing | 4.175 | 7.92 | 140.182 | 37.432 | 24.59 | 100 <from template> | 0 <from template> | 0 | 0 | Yes <from template> | [28 empty] | F.14a Showers | 19 | 18.78 | -0.0757 | -0.1983 | 0 | 0 | -0.163 | 0 | 0.437 | 0.437 | 0
HL000001 | 48 | F.17 Female Changing | 4.175 | 7.92 | 141.03 | 37.658 | 24.66 | 100 <from template> | 0 <from template> | 25.293 | 0 | Yes <from template> | [28 empty] | F.14 Male Changing | 19 | 18.87 | -0.1335 | -0.1643 | 0 | 0 | -0.2857 | 0 | 0.5834 | 0.583 | 0
F1000001 | 49 | F.17a Showers | 4.175 | 7.92 | 80.454 | 21.483 | 18.86 | 100 <from template> | 0 <from template> | 14.429 | 0 | Yes <from template> | [28 empty] | F.17 Female Changing | 19 | 18.88 | -0.2668 | -0.0221 | 0 | 0 | -0.2874 | 0 | 0.5763 | 0.576 | 0
G0000002 | 50 | G.06 Waiting Area | 0 | 4.175 | 484.891 | 116.142 | 57.21 | 100 <from template> | 0 <from template> | 29.81 | 0 | Yes <from template> | [28 empty] | F.17a Showers | 19 | 18.78 | -0.1513 | -0.1208 | 0 | 0 | -0.164 | 0 | 0.4361 | 0.436 | 0
XT000001 | 51 | F.19 Refuge | 4.175 | 7.92 | 64.105 | 17.117 | 17.26 | 100 <from template> | 0 <from template> | 32.316 | 0 | Yes <from template> | [28 empty] | G.06 Waiting Area | 18 | 17.89 | -0.9905 | -0.0543 | 0 | -0.4891 | -0.947 | 0 | 2.4809 | 2.481 | 0
[41 empty] | F.19 Refuge | 18 | 17.8 | -0.2196 | 0 | 0 | 0 | -0.1252 | 0 | 0.3448 | 0.345 | 0

## IES + Revit Name Check
Instance:Name | Instance:Number | Instance:Area | Combined Number + Name | IES Name | Possible Match
Assisted Changing Room | G.12 | 11.95 m² | G.12 Assisted Changing Room
Pool Cleaner | G.24 | 4.81 m² | G.24 Pool Cleaner |  | G.24 Pool Clean
Pool Store | G.25 | 18.06 m² | G.25 Pool Store | G.25 Pool Store
Plant | G.23 | 182.48 m² | G.23 Plant | G.23 Plant
Stair | G.21 | 16.02 m² | G.21 Stair | G.21 Stair
Squash Court | G.17 | 62.72 m² | G.17 Squash Court | G.17 Squash Court
Squash Court | G.18 | 62.70 m² | G.18 Squash Court | G.18 Squash Court
Store | G.22 | 20.27 m² | G.22 Store | G.22 Store
WC's | G.07 | 19.44 m² | G.07 WC's | G.07 WC's
WC's | G.08 | 14.60 m² | G.08 WC's | G.08 WC's
WC's | G.10 | 29.20 m² | G.10 WC's | G.10 WC's
Office | G.02 | 15.55 m² | G.02 Office | G.02 Office
Gym | G.20 | 339.71 m² | G.20 Gym | G.20 Gym
Squash Court | G.19 | 62.72 m² | G.19 Squash Court | G.19 Squash Court
Pool | G.01 | 325.39 m² | G.01 Pool | G.01 Pool
WC's | G.09 | 42.37 m² | G.09 WC's | G.09 WC's
Gym High Level |  | 339.76 m² | Gym High Level
Health Related Fitness | F.08 | 87.16 m² | F.08 Health Related Fitness | F.08 Health Related Fitness
Store | F.11 | 6.05 m² | F.11 Store | F.11 Store
HRE Office | F.09 | 9.97 m² | F.09 HRE Office | F.09 HRE office
Male WC's | F.15 | 19.69 m² | F.15 Male WC's | F.15 Male WC's
Female WC's | F.16 | 20.31 m² | F.16 Female WC's | F.16 Female WC's
External Plant |  | 75.47 m² | External Plant
Male Changing | F.14 | 38.06 m² | F.14 Male Changing | F.14 Male Changing
Female Changing | F.17 | 39.31 m² | F.17 Female Changing | F.17 Female Changing
Store | F.05 | 10.90 m² | F.05 Store | F.05 Store
Stair | F.21 | 5.42 m² | F.21 Stair | F.21 Stair
Dance Studio | F.07 | 102.36 m² | F.07 Dance Studio | F.07 Dance Studio
Classroom | F.10 | 61.13 m² | F.10 Classroom | F.10 Classroom
External Plant |  | 145.50 m² | External Plant
Pool High Level |  | 540.18 m² | Pool High Level
Fitness Centre | F.03 | 302.59 m² | F.03 Fitness Centre | F.03 Fitness Centre
Squash Court High Level |  | 268.25 m² | Squash Court High Level
Lobby | G.03 | 19.62 m² | G.03 Lobby | G.03 Lobby
Waiting Area | G.06 | 119.12 m² | G.06 Waiting Area | G.06 Waiting Area
Classroom | G.29 | 36.90 m² | G.29 Classroom |  | G.29 Classroom/ Waiting Area
Circulation | G.15 | 29.88 m² | G.15 Circulation | G.15 Circulation
Flexible Use Area | G.16 | 71.67 m² | G.16 Flexible Use Area | G.16 Flexible Use Area
Circulation | F.01 | 183.68 m² | F.01 Circulation | F.01 Circulation
Circulation | F.02 | 27.79 m² | F.02 Circulation | F.02 Circulation
Refuge | F.19 | 17.39 m² | F.19 Refuge | F.19 Refuge
Store | F.06 | 6.86 m² | F.06 Store | F.06 Store
Accessible W.C. | F.13 | 3.58 m² | F.13 Accessible W.C. | F.13 Accessible W.C.
Accessible Changing Room | F.12 | 7.47 m² | F.12 Accessible Changing Room | F.12 Accessible Changing Room
Showers | F.14a | 17.79 m² | F.14a Showers | F.14a Showers
Showers | F.17a | 18.38 m² | F.17a Showers | F.17a Showers
Unisex Changing Room | G.13 | 8.06 m² | G.13 Unisex Changing Room
Accessible Changing Room | G.14 | 6.72 m² | G.14 Accessible Changing Room
Space |  | Not Placed | Space
Changing Village | G.11 | 226.75 m² | G.11 Changing Village | G.11 Changing Village
Riser |  | 6.47 m² | Riser
Circulation | G.26 | 272.33 m² | G.26 Circulation | G.26 Circulation
Pool Surround | G.01A | 157.84 m² | G.01A Pool Surround
Room | F.22 | 5.61 m² | F.22 Room
Room | F.23 | 4.52 m² | F.23 Room
Room | F.21 | 3.12 m² | F.21 Room |  | F.21 Stair
Room | F.19 | 16.26 m² | F.19 Room |  | F.19 Refuge
Room | F.14b | 2.03 m² | F.14b Room

## Revit Data
|  |  |  | Cooling |  | Heating
Instance:Name | Instance:Number | Instance:Area | Combined Name + Number | Required Sensible Output | Required Total Output | Required Output
Assisted Changing Room | G.12 | 11.95 m² | G.12 Assisted Changing Room
Pool Cleaner | G.24 | 4.81 m² | G.24 Pool Cleaner
Pool Store | G.25 | 18.06 m² | G.25 Pool Store |  |  | 821.905
Plant | G.23 | 182.48 m² | G.23 Plant |  |  | 3305.33
Stair | G.21 | 16.02 m² | G.21 Stair |  |  | 845.825
Squash Court | G.17 | 62.72 m² | G.17 Squash Court |  |  | 1861.39
Squash Court | G.18 | 62.70 m² | G.18 Squash Court |  |  | 788.095
Store | G.22 | 20.27 m² | G.22 Store |  |  | 948.98
WC's | G.07 | 19.44 m² | G.07 WC's |  |  | 1391.155
WC's | G.08 | 14.60 m² | G.08 WC's |  |  | 256.22
WC's | G.10 | 29.20 m² | G.10 WC's |  |  | 513.705
Office | G.02 | 15.55 m² | G.02 Office |  |  | 1102.62
Gym | G.20 | 339.71 m² | G.20 Gym |  |  | 15106.515
Squash Court | G.19 | 62.72 m² | G.19 Squash Court |  |  | 2220.765
Pool | G.01 | 325.39 m² | G.01 Pool |  |  | 43112.695
WC's | G.09 | 42.37 m² | G.09 WC's |  |  | 987.85
Gym High Level |  | 339.76 m² | Gym High Level
Health Related Fitness | F.08 | 87.16 m² | F.08 Health Related Fitness |  |  | 3933.805
Store | F.11 | 6.05 m² | F.11 Store |  |  | 125.465
HRE Office | F.09 | 9.97 m² | F.09 HRE Office |  |  | 535.785
Male WC's | F.15 | 19.69 m² | F.15 Male WC's |  |  | 345.46
Female WC's | F.16 | 20.31 m² | F.16 Female WC's |  |  | 344.655
External Plant |  | 75.47 m² | External Plant
Male Changing | F.14 | 38.06 m² | F.14 Male Changing |  |  | 671.025
Female Changing | F.17 | 39.31 m² | F.17 Female Changing |  |  | 662.745
Store | F.05 | 10.90 m² | F.05 Store |  |  | 1723.735
Stair | F.21 | 5.42 m² | F.21 Stair |  |  | 723.925
Dance Studio | F.07 | 102.36 m² | F.07 Dance Studio |  |  | 4650.255
Classroom | F.10 | 61.13 m² | F.10 Classroom |  |  | 1841.955
External Plant |  | 145.50 m² | External Plant
Pool High Level |  | 540.18 m² | Pool High Level
Fitness Centre | F.03 | 302.59 m² | F.03 Fitness Centre |  |  | 5147.86
Squash Court High Level |  | 268.25 m² | Squash Court High Level
Lobby | G.03 | 19.62 m² | G.03 Lobby |  |  | 1728.91
Waiting Area | G.06 | 119.12 m² | G.06 Waiting Area |  |  | 2290.57
Classroom | G.29 | 36.90 m² | G.29 Classroom
Circulation | G.15 | 29.88 m² | G.15 Circulation |  |  | 920
Flexible Use Area | G.16 | 71.67 m² | G.16 Flexible Use Area |  |  | 3045.775
Circulation | F.01 | 183.68 m² | F.01 Circulation |  |  | 3839.39
Circulation | F.02 | 27.79 m² | F.02 Circulation |  |  | -474.49
Refuge | F.19 | 17.39 m² | F.19 Refuge |  |  | 958.985
Store | F.06 | 6.86 m² | F.06 Store |  |  | 151.225
Accessible W.C. | F.13 | 3.58 m² | F.13 Accessible W.C. |  |  | 128.685
Accessible Changing Room | F.12 | 7.47 m² | F.12 Accessible Changing Room |  |  | 207.46
Showers | F.14a | 17.79 m² | F.14a Showers |  |  | 502.55
Showers | F.17a | 18.38 m² | F.17a Showers |  |  | 501.515
Unisex Changing Room | G.13 | 8.06 m² | G.13 Unisex Changing Room
Accessible Changing Room | G.14 | 6.72 m² | G.14 Accessible Changing Room
Space |  | Not Placed | Space
Changing Village | G.11 | 226.75 m² | G.11 Changing Village |  |  | 10459.25
Riser |  | 6.47 m² | Riser
Circulation | G.26 | 272.33 m² | G.26 Circulation |  |  | 4217.625
Pool Surround | G.01A | 157.84 m² | G.01A Pool Surround
Room | F.22 | 5.61 m² | F.22 Room
Room | F.23 | 4.52 m² | F.23 Room
Room | F.21 | 3.12 m² | F.21 Room
Room | F.19 | 16.26 m² | F.19 Room
Room | F.14b | 2.03 m² | F.14b Room